## Vollständige Daten
Model | BHW-10 | BHW-12 | BHW-15
PV Input
Recommended Max. PV Input Power [Wp] | 13000 | 15600 | 18750
Max. Input Voltage [V] | 1000
MPPT Voltage Range [V] | 180~950
Rated Voltage [V] | 600
Start-up Voltage [V] | 200
No. of MPP-Trackers | 2
No. of PV Strings per MPPT | 2/1
Max. Input Current per MPPT [A] | 30/15
Max. Short-Circuit Current per MPPT [A] | 36/18
AC Output
Rated Output Power [W] | 10000 | 12000 | 15000
Rated Output Current [A] | 14.5 | 17.4 | 21.7
Max. Output Current [A] | 16 | 19 | 23.8
Max. Apparent Output Power [VA] | 11000 | 13200 | 16500
Rated Output Voltage [V] | 220/380;230/400
Rated Grid Frequency [Hz] | 50/60
Power Factor [cos φ] | 1/0.8( leading)~0.8(lagging)
THDi (@Rated Output Power ) | ＜3%
AC Input (Grid)
Max. Apparent Input Power [VA] | 11000 | 13200 | 16500
Max. Input Current [A] | 16 | 19 | 23.8
Rated Output Voltage [V] | 220/380;230/400
Rated Grid Frequency [Hz] | 50/60
Battery
Battery Module Type | Lithium Iron Phosphate (LiFePO4)
Battery Voltage Range [V] | 150-600
Maximum Charge/Discharge Current [A] | 25
Battery Communication | CAN
AC Output (Off-Grid )
Rated Output Power [W] | 10000 | 12000 | 15000
Rated Output Voltage[V] | 220/380;230/400
Rated Output Frequency [Hz] | 50/60
Rated Output Current[A] | 14.5 | 17.4 | 21.7
THDi (Rated Output Power) | ＜3%
Switch Time [ms] | ＜10
Peak Apparent Power , Duration [VA, s] | 15000, 30 | 18000, 30 | 22500, 30
Efficiency
Max. Efficiency | 98%
Euro Efficiency | 97,3%
Charging/Discharging Efficiency of the Battery | 98.5%@Charge/97.0%@Discharge
Protection
DC-Schalter | Integrated
Insulation Resistance Detection | Integrated
Input Reverse Polarity Protection | Integrated
Anti-island Protection | Integrated
Residual Current Monitoring | Integrated
Overtemperature Protection | Integrated
DC Surge Protection | Integrated (Type II）
AC Surge Protection | Integrate (Type II）
General Data
Dimensions (W×H×D) [mm] | 498 × 563 × 200
Weight [kg] | 28 | 28 | 29
Display | LCD / WEB / APP
Communication | WIFI / RS485 / LAN
Operating Temperature Range [℃] | -25~60
Relative Humidity | 0%~100%, Non-condensing
Operation Altitude[m] | ≤4000 (Derating above 2000)
Self Consumption (night) [W] | ＜15
Topology | Transformerless
Cooling Concept | Natural Convection | Natural Convection | Smart fan-cooling
Ingress Protection (IP) Rating | IP66
Warranty | 10 Years
Certification | VDE 4105; IE+A1:D65+A1:D65C 62109-1/2; IEC 62477-1; IEC 61000-6-1/2/3/4; CE

## Daten für Broschüre
| BHW-10 | BHW-12 | BHW-15
Nenn-Ausgangsleistung [kW] | 10 | 12 | 15
Max. PV-Generatorleistung [kWp] | 13 | 15,6 | 18,75
Max. DC-Eingangsspannung [V] | 1000
Start-Eingangsspannung [V] | 200
DC-MPP-/DC-Batterie-Arbeitsspannungsbereich [V] | 180~950
Anzahl der MPP-Tracker | 2
Anzahl der PV-String pro MPPT | 2/1
Netzanschluss [Ph/V/Hz] | 3-phasig/400V/50Hz
Nennausgangsleistung (Notstrom) [kW] | 10 | 12 | 15
Max. Wirkungsgrad | 98%
Produktmaße (B×H×T) [mm] | 498 × 563 × 200
Gewicht [kg] | 28 | 28 | 29
Betriebstemperaturbereich [℃] | -25 ~ 60
Schutzart | IP66
Grantie | 10 Jahre
Zertifikate | VDE 4105; IE+A1:D65+A1:D65C 62109-1/2; IEC 62477-1; IEC 61000-6-1/2/3/4; CE